Citect for Windows

Driver Specification

DACard Driver

Data Acquisition Card ACL-812PG

| Author | Date | Comment |
| --- | --- | --- |
| Andreas Verhamme | 30/10/1998 | Data Acquisition Card |

Contents

1.	Target Device and Protocol	3

1.1	Introduction	3

1.2	Device Manufacturer	3

1.3	Device Definition	3

1.4	Communications Method	3

1.5	Communications/Hardware Configuration	3

1.5.1	Software Setup	4

1.6	Maximum Request Length	4

2.	User Interface	5

2.1	Introduction	5

2.2	Driver Name	5

2.3	Boards Form	5

2.3.1	Board Type	5

2.3.2	Address	5

2.3.3	IO Port	5

2.3.4	Interrupt	5

2.3.5	Special Opt	5

2.4	Ports Form	5

2.5	IO Devices Form	7

2.5.1	Protocol	7

2.5.2	Address	7

2.6	IO Device Variable Types	8

2.6.1	Formats and types	8

2.7	PROTDIR.DBF	8

2.8	Parameters and INI options	8

2.8.1	Standard Parameters	8

2.8.2	Driver Specific Parameters	8

3.	Performance Testing	9

3.1	Performance	9

4.	Contacts	10

4.1	Contacts	10

# Target Device and Protocol

## Introduction

This section defines the types of I/O Devices that are targeted by this driver.

## Device Manufacturer

ADCLONE or ADVANTECH

## Device Definition

Enhanced Multi-Function Data Acquisition Card   ACL – 812PG

Enhanced Multi-Function Data Acquisition Card   PCL – 812

- 16 Digital Inputs

- 16 Digital Outputs

- 16 Analog Inputs (-10V to +10V)

- 2 Analog Outputs (0V to +10V)

- 1 Counter

## Communications Method

Proprietary board

## Communications/Hardware Configuration

The ACL-812PG requires 16 consecutive address locations in the I address space. The address is restricted by the following conditions.

- The base address must be within the range 200hex to 3F0hex.(Default = 220Hex).

- The base address should not conflict with any PC reserved I/O address.

See the manual of the Data Acquisition Card to setup the Base Address and the Jumpers.

The driver doesn’t support DMA. Setup the DMA Jumpers DRQ and DACK to no DMA (JP6 and JP7).

The driver doesn’t support A/D conversion on interrupt. Setup the Interrupt Jumper IRQ (JP12 and JP5) to NO INTERRUPT.

To use the Analog A/D conversion setup the TRIGGER Jumper JP1 to internal and the CLOCK Jumper JP2 (Clock 2MHz) to internal.

When using the Counter function you must setup the TRIGGER Jumper JP1 to internal and the CLOCK Jumper JP2 to external. (NOTE: In this case you cannot use the A/D conversion !)

Setup the Reference Voltage for Analog Inputs to –5V or –10V by Jumper JP8. The Reference Voltage for the Analog Outputs must be setup to –5V or –10V by Jumper JP9.

### Software Setup

No driver or additional software has to be installed on the PC (Windows 95 or Windows NT 4.0).

## Maximum Request Length

The maximum request length should be left to 16 WORDS, which allows the driver to read the 16 Analog inputs at one time. The 16 Digital Inputs/Outputs are always read in one cycle.

# User Interface

## Introduction

This section defines how the user will see the driver.  This relates directly to how the Citect forms need to be filled out and any special INI options.  For the kernel, the debug trace messages and the Stats.Special counters are documented.

## Driver Name

DACARD

## Boards Form

### Board Type

DACard

### Address

Do not assign this field.

### IO Port

0x220 to 0x3F0.  (Default address is 0x220)

### Interrupt

Do not assign this field.

### Special Opt

Do not assign this field.

## Ports Form

## IO Devices Form

### Protocol

DACARD

### Address

Must be 1.

NOTE: Only one Board may be used !

## IO Device Variable Types

### Formats and types

See DACARD.DBF in the Citet\Bin directory:

| TEMPLATE | UNIT_TYPE | RAW_TYPE | BIT_WIDTH | LOW | HIGH | COMMENT |
| --- | --- | --- | --- | --- | --- | --- |
| DI%U | 1 | 0 | 1 | 0 | 15 | Digital Input |
| DO%U | 2 | 0 | 1 | 0 | 15 | Digital Ouput |
| AI%U | 3 | 1 | 16 | 0 | 15 | Analog Input |
| AO%U | 4 | 1 | 16 | 0 | 1 | Analog Ouput |
| CN%U | 5 | 1 | 16 | 1 | 1 | Counter 1 |

## PROTDIR.DBF

{What entry needs to be added to the PROTDIR.DBF for this protocol.}

| TAG | FILE | BIT_BLOCK | MAX_LENGTH | OPTIONS |
| --- | --- | --- | --- | --- |
| Dacard | Dacard | 512 | 512 | 0x17f |

## Parameters and INI options

### Standard Parameters

Block

Delay=0

MaxPending=2

Polltime=2

Timeout=400

Retry=2

WatchTime=10

### Driver Specific Parameters

The following parameters can be used to test the board:

Debug=1                          Shows all messages at startup of the driver.

SimulateDACard=1          To test the driver without any board in the PC.

SimulateAnaOutputs=1    To force the Analog outputs by the driver.

SimulateDigOutputs=1     To force the Digital outputs by the driver.

# Performance Testing

## Performance

The Data Acquisition Card Adclone 812PG has been test at IP SYSTEMES. The results of these test can give you an idea of the limits of this card. Please keep on mind that CITECT is not a real time acquisition system. The performance of the DACARD driver may decrease extremely if you display to many Tags at a time on one page or simply when your computer is busy with other applications (when you open too many application at a time, like EXCEL, Tetris, WORD, etc).

The performance test has been done at IP SYSTEMES under the following conditions:

- Pentium 166Mhz

- Windows NT 4.0 (and Windows 95)

- Citect Version 5.10

Test Results :

| Test | Refresh time |
| --- | --- |
| Trending of 1Digital Inputs and 1 Digital Outputs | 10 ms |
| Display of 16 Digital Inputs and 16 Digital Outputs on a normal page | 50 ms (Minimum page scantime of Citect) |
| Trending of 1 Analog Inputs and 1 Analog Outputs | 12-15 ms |
| Trending of 16 Analog Inputs | 26-29 ms |
| Display of 16 Analog Inputs and 2 Outputs on a normal page | 50 ms (Minimum page scantime of Citect) |
| Trending of 1Counter | 10 ms |
| Mixed page with 16 Digital Inputs/Outputs, 16 Analog puts, 2 Analog Outputs | 50 ms (Minimum page scantime of Citect) |

# Contacts

## Contacts

Andreas Verhamme IP SYSTEMES France

Email: Andreas.verhamme@ip-systemes.fr