## DTFormatter

Formats DriverTrace output

Version: 3.4

Requirements:
CitectSCADA version 5.41 +, .Net version 1 +

Description:

This utility formats and exports DriverTrace output from the syslog.dat files allowing you to more easily find problems IO related problems.  Refer to CitectSCADA KnowledgeBase for further information on DriverTrace.

The utility will:

- Place a reply for a request immediately below the request. 
i.e. the ← REPLY matched up with the original REQUEST →

- Flag missing replies with ### Reply MISSING

- Mark where DCBs have returned errors with a ### flag.

- Document known error codes with the error message.

- Filter traces by specifying a filter flag 
e.g. CTDRV_WRITE in the case sensitive box would result in only CTDRV_WRITE DCBs being in the trace.

Notes:

- Drag & drop features - The light blue fields support drag and drop from your explorer.  Drag the file and drop it into the field and the program will remember its path.

- The level of instrumenting the syslog.dat depends on access to a "proterr.dbf" file (in xx\citectxx\bin) and your projects "units.dbf" file.
Provided proterr.dbf has been updated, custom drivers not distributed by Citect will also be instrumented.

- Tick Box Meanings:
Mark Errors - Places a "###" marker in the file to make it easy to find errors
Error Text - Will place textual descriptions of errors next to an error
Separate requests - Places a blank line between driver requests to make it easier to read the file
Include other lines - Does not filter out other syslog messages besides drivertraces.

- DCB Filters:
Allows results to be filtered based on a match in the "=> xxx" line. e.g. "unit10" would output only traces with "unit10" in them.

- If the trace contains Drivertraces then the utility will extract the Port to Protocol relationship automatically to allow instrumentation of error codes.

- If only normal IO Server syslog messages exist in the log (no drivertraces), then the project Units.dbf can be used to provide this mapping.

- Units.dbf use – You can optionally drag and drop the Units.dbf for the project to provide the mapping between any unreferenced Ports and Protocols. This allows the maximum number of errors to be decoded.

- Ticking “Separate requests” can make reading the traces easier.

- Always try to get the units.dbf, ports.dbf files (or the compiled versions _units.rdb and _ports.rdb files if the DBF is not available) associated with the syslog.dat.

- Special note on “CTDRV_INFO”
This trace does not have a return and currently incorrectly gets assigned a missing return marker. This will be fixed in a later version.

- ProtErr.dbf
The system uses proterr.dbf to be able to map a protocol error to an actual text string.  It will use the protdir.dbf under your citect\bin install by default.

- Console Mode.
Just pass the path to the syslog.dat file and it will create the <filepath>.txt output without using the GUI. 

E.g. dtformatter c:\windows\syslog.dat

will produce a file c:\windows\syslog.dat.txt with items instrumented.

- You may need a local copy of the utility due to .NET permission issues (a crash with reference to a “security exception” is a dead giveaway). We suggest in your \windows area.

- It is not recommended that DTFormatter be used on very large syslog.dat files (20Mb +) as it places every line into memory.

Example:

Syslog.dat extract:

-> 3094C :30.860 Cmd: 02 CTDRV_INIT_CHANNEL,ABCLX, Port: B4T1_S858, Unit: N/A

-> 95B9C :30.861 Cmd: 02 CTDRV_INIT_CHANNEL,ABCLX, Port: B4T1_S857, Unit: N/A

-> C123C :30.861 Cmd: 02 CTDRV_INIT_CHANNEL,ABCLX, Port: B4T1_S851, Unit: N/A

-> EE614 :30.861 Cmd: 02 CTDRV_INIT_CHANNEL,ABCLX, Port: B4T1_S852, Unit: N/A

-> 18E0C :30.861 Cmd: 02 CTDRV_INIT_CHANNEL,ABCLX, Port: B4T1_S269, Unit: N/A

<-2CB74 :30.861 Cmd: 02 CTDRV_INIT_CHANNEL ErrDriver 0 (0x0) and took 0ms

<-3094C :30.861 Cmd: 02 CTDRV_INIT_CHANNEL ErrDriver 536870937 (0x20000019) and took 0ms

<-95B9C :30.861 Cmd: 02 CTDRV_INIT_CHANNEL ErrDriver 536870937 (0x20000019) and took 0ms

<-C123C :30.861 Cmd: 02 CTDRV_INIT_CHANNEL ErrDriver 536870937 (0x20000019) and took 0ms

<-EE614 :30.862 Cmd: 02 CTDRV_INIT_CHANNEL ErrDriver 536870937 (0x20000019) and took 0ms

<-18E0C :30.862 Cmd: 02 CTDRV_INIT_CHANNEL ErrDriver 536870937 (0x20000019) and took 0ms

Thu Jun 14 15:21:59 2007 308:25:30.861 Error: Channel not yet initialized

CINIT    0017    B4T1_S858       PLC858                 Error_in_CMD-2   16

Generic 000023 Driver 536870937 (0x20000019)

Thu Jun 14 15:21:59 2007 308:25:30.861 Error: Channel not yet initialized

CINIT    0017    B4T1_S857       PLC857                 Error_in_CMD-2   16

Generic 000023 Driver 536870937 (0x20000019)

Thu Jun 14 15:21:59 2007 308:25:30.861 Error: Channel not yet initialized

CINIT    0017    B4T1_S851       PLC851                 Error_in_CMD-2   16

Generic 000023 Driver 536870937 (0x20000019)

Thu Jun 14 15:21:59 2007 308:25:30.862 Error: Channel not yet initialized

CINIT    0017    B4T1_S852       PLC852                 Error_in_CMD-2   16

Generic 000023 Driver 536870937 (0x20000019)

Thu Jun 14 15:21:59 2007 308:25:30.862 Error: Channel not yet initialized

CINIT    0017    B4T1_S269       PLC269                 Error_in_CMD-2   16

Generic 000023 Driver 536870937 (0x20000019)

Output

-> 3094C :30.860 Cmd: 02 CTDRV_INIT_CHANNEL,ABCLX, Port: B4T1_S858, Unit: N/A

<-3094C :30.861 Cmd: 02 CTDRV_INIT_CHANNEL ### ErrDriver 536870937 (0x20000019) and took 0ms

### Drivertrace: Protocol ABCLX, Port: B4T1_S858, Unit: N/A Error 536870937 - "Database initilisation in progress"

-> 95B9C :30.861 Cmd: 02 CTDRV_INIT_CHANNEL,ABCLX, Port: B4T1_S857, Unit: N/A

<-95B9C :30.861 Cmd: 02 CTDRV_INIT_CHANNEL ### ErrDriver 536870937 (0x20000019) and took 0ms

### Drivertrace: Protocol ABCLX, Port: B4T1_S857, Unit: N/A Error 536870937 - "Database initilisation in progress"

-> C123C :30.861 Cmd: 02 CTDRV_INIT_CHANNEL,ABCLX, Port: B4T1_S851, Unit: N/A

<-C123C :30.861 Cmd: 02 CTDRV_INIT_CHANNEL ### ErrDriver 536870937 (0x20000019) and took 0ms

### Drivertrace: Protocol ABCLX, Port: B4T1_S851, Unit: N/A Error 536870937 - "Database initilisation in progress"

-> EE614 :30.861 Cmd: 02 CTDRV_INIT_CHANNEL,ABCLX, Port: B4T1_S852, Unit: N/A

<-EE614 :30.862 Cmd: 02 CTDRV_INIT_CHANNEL ### ErrDriver 536870937 (0x20000019) and took 0ms

### Drivertrace: Protocol ABCLX, Port: B4T1_S852, Unit: N/A Error 536870937 - "Database initilisation in progress"

-> 18E0C :30.861 Cmd: 02 CTDRV_INIT_CHANNEL,ABCLX, Port: B4T1_S269, Unit: N/A

<-18E0C :30.862 Cmd: 02 CTDRV_INIT_CHANNEL ### ErrDriver 536870937 (0x20000019) and took 0ms

### Drivertrace: Protocol ABCLX, Port: B4T1_S269, Unit: N/A Error 536870937 - "Database initilisation in progress"

Thu Jun 14 15:21:59 2007 308:25:30.861 Error: Channel not yet initialized

CINIT    0017    B4T1_S858       PLC858                 Error_in_CMD-2   16

Generic 000023 Driver 536870937 (0x20000019)

### IOServer: Protocol ABCLX Error 536870937 - "Database initilisation in progress"

Thu Jun 14 15:21:59 2007 308:25:30.861 Error: Channel not yet initialized

CINIT    0017    B4T1_S857       PLC857                 Error_in_CMD-2   16

Generic 000023 Driver 536870937 (0x20000019)

### IOServer: Protocol ABCLX Error 536870937 - "Database initilisation in progress"

Thu Jun 14 15:21:59 2007 308:25:30.861 Error: Channel not yet initialized

CINIT    0017    B4T1_S851       PLC851                 Error_in_CMD-2   16

Generic 000023 Driver 536870937 (0x20000019)

### IOServer: Protocol ABCLX Error 536870937 - "Database initilisation in progress"

Thu Jun 14 15:21:59 2007 308:25:30.862 Error: Channel not yet initialized

CINIT    0017    B4T1_S852       PLC852                 Error_in_CMD-2   16

Generic 000023 Driver 536870937 (0x20000019)

### IOServer: Protocol ABCLX Error 536870937 - "Database initilisation in progress"