Cicode Programming Reference > Functions Reference

## V6.10, V7, V7.10 TagDebug

Displays a dialog which allows you to select from a list (to a maximum of 256 tags) of configured variable tags in your system for Read / Write operations.  This function is useful for debugging or commissioning. Both variable tags (globally available) and local tags (values per process) and available for read / write operations.

The tag name can be selected or typed in. The value field will show the read value or an error code, and can be used to enter the data to write. The form is below.  :

Each time the “Read” or “Write” button is pressed, the “Last request” time is updated to show when the request was made.  The engineering units abbreviations are as follows  :

RZ – Raw Zero,  RF – Raw Full Scale,  EZ – Engineering Zero,  EF – Engineering Full Scale

“Help” will take you to the Help on cicode error codes.

Tip! When you change a tag name, the values shown on the form will not be valid until a Read or Write operation is done.

Tip! When entering data into the Value or MS field, use a <return> to ensure the data is updated.

The form allows for reads to be repeated. Adjust the read time in milliseconds next to the “Auto Read” button and click on “Auto Read”. “Stop Read” naturally stops this operation.

The form includes displaying the error as seen here where the Tag entered did not exist. However other errors are possible and that is where the “Tag’s Device Status”  is handy. This will show the state of the device the tag is on. E.g. the device could be “OFFLINE”.

Tag filtering – To make the pull down box usable, a limit of 256 items has been imposed. Thus if the tag you want to read is not available you can simply enter its name, or filter the complete tag database for your  tags,  e.g. you might have tags in process loops with the prefix “LOOP”. Click on “Filter”, enter your string, then click on “OK” then the close X. Now the pull down will have the first 256 tags with LOOP in the name.  “Clear” can be used to clear the filter.

Note: The text entered can be a common suffix, it does not need to be the start of tag names.

Filter flag: A “F” to the left of the “Filter” button indicates a filter is currently in effect. The “*” that no filter is in effect. Note: This item is deliberately a button (the first) as an <Enter> in other edit forms fires the first button on a Form. This then ensures the correct operation is done by clicking.

Note: It is possible for the tag name Combobox to show manually entered tags after filter changes. This is because no “clear all entries” operation is available in Formxxx() functions. The Combobox is cleared by deleting tags based on the previous filter.

Tag Write Note:

When a write is done, the syslog.dat file has an log entry added similar to :

<timestamp> TagDebug() Write: User 'Engineer' set tag 'Entry_ScrapWeight' to value ' 23.00' - NO ERROR

## V7.20 TagDebugEx

Displays a dialog which allows you to select from a list (to a maximum of 512 tags) of configured variable tags in your system for Read / Write operations.  This function is useful for debugging or commissioning. Both variable tags (globally available) and local tags (values per process) and available for read / write operations. v7.20 supports Tag Extensions.

The tag name can be selected or typed in. The value field will show the read value or an error code, and can be used to enter the data to write. The form is below.  :

NB: In the above example, the device status info is refreshed only when the “Tag’s Device Status” button is pressed.

Each time the “Read” or “Write” button is pressed, the “Last request” time is updated to show when the request was made.  The engineering units abbreviations are as follows  :

RZ – Raw Zero,  RF – Raw Full Scale,  EZ – Engineering Zero,  EF – Engineering Full Scale

“ErrHelp” will take you to the Help on cicode error codes.

“TagExtHelp” will bring up the tag extensions help.

Tag Extensions - As you can see, tag extensions are available in the pull down. For the automatic display of properties, this should be used instead of manually entering the extension to the tag name.

After the “Read” you get this…

Tag Properties

The “read” value is effectively the .V value, the .Q is the tag Quality, .QT the Quality timestamp, .VT the value timestamp, and .T the overall object timestamp which is the most recent of the two timestamps.

Array Handling – The extended properties for arrays will only work if the “index” field is used, NOT if “TagExt_DemoTag1.Override[10]” is manually added into the tag  field box.

In this example TagExt_ArrayDemo.Override[10] was read.

Tip! When you change a tag name, the values shown on the form will not be valid until a Read or Write operation is done.

Tip! When entering data into the Value or MS field, use a <return> to ensure the data is updated.

The form allows for reads to be repeated. Adjust the read time in milliseconds next to the “Auto Read” button and click on “Auto Read”. “Stop Read” naturally stops this operation.

The form includes displaying the error as seen here where the Tag entered did not exist. However other errors are possible and that is where the “Tag’s Device Status”  is handy. This will show the state of the device the tag is on. E.g. the device could be “OFFLINE”.

Tag filtering – To make the pull down box usable, a limit of 256 items has been imposed. Thus if the tag you want to read is not available you can simply enter its name, or filter the complete tag database for your  tags,  e.g. you might have tags in process loops with the prefix “LOOP”. Click on “Filter”, enter your string, then click on “OK” then the close X. Now the pull down will have the first 256 tags with LOOP in the name.  “Clear” can be used to clear the filter.

Note: The text entered can be a common suffix, it does not need to be the start of tag names.

Filter flag: A “F” to the left of the “Filter” button indicates a filter is currently in effect. The “*” that no filter is in effect. Note: This item is deliberately a button (the first) as an <Enter> in other edit forms fires the first button on a Form. This then ensures the correct operation is done by clicking.

Note: It is possible for the tag name Combobox to show manually entered tags after filter changes. This is because no “clear all entries” operation is available in Formxxx() functions. The Combobox is cleared by deleting tags based on the previous filter.

Tag Write Note:

When a write is done, the syslog.dat file has an log entry added similar to :

<timestamp> TagDebug() Write: User 'Engineer' set tag 'Entry_ScrapWeight' to value ' 23.00' - NO ERROR