# CitectSCADA Trend Conversion Tool Help

IMPORTANT NOTICE: The conversion trend tool is not part of a software release from Schneider Electric. It has been developed outside the normal product development process control as is supplied AS IS. Please read the “Before Using” section below before use.

## Overview

TrendConvert was developed to convert CitectSCADA Periodic trends (plus Periodic Event) into Event trends. This utility will not change you current running system. After use of the program new files are created which need to be moved to replace existing files.

The user has the option to keep the trends in the same data size, force them to be 2 or 8 byte in size. (Note: Our “2 byte” event trend is actually internally 4 bytes but the “2 byte” name is the historical reference).

A sub directory is used to place the new files in and an XML file is created with the trend record changes in it. This file will be able to be used in EXCEL to adjust the Trend.DBF file later.

This utility should be compatible for trends created under v6.10 to v7.40. The tool is written in C# and has interfacing code in C to talk to the existing CitectSCADA trend system. Thus the reading and writing of trends should be subject to the same range of problems or issues that can arise during CitectSCADAs use of the trend system.

It is recommended you do a “Report” run first to see if there are any issues

Here is a Periodic Trend

And the Event Trend produced After

## Testing and Release Status Statement

This tool has not gone through the normal development cycle for CitectSCADA products. It has had limited QA testing on a set of data which may not represent the full range of possibilities. Tool has been tested so far under v6.10 & v7.10 using the default [Trend]AllFiles mode. It has been tested on a run of 2000 trends. The normal precaution with all “upgrade” tools applies to have a full backup of your existing data prior to using the software. This tool is NOT a released product and is not supported by Citect Support. In the context of Beta users or trial users, it will be supported by the SCADA Activity group.

The tool is designed to be used while CitectSCADA trends are not actively being used on the PC (e.g. the trend server should not be running during conversion).  The tool does NOT change your current project configuration or data but creates new files for you to use.

## How to Install

A manual install is needed. The two files TrendConvert.exe and TrendAccess.dll need to be copied to the CitectSCADA\bin directory. A Shortcut can be made to TrendConvert.exe  making the working directory the CitectSCADA\bin directory.

## How to Run

- The tool should NOT be run while CitectSCADA is running. This information is accurate for v 1.41 of the utility.

v1.41 Look

- Before running – Backup your trend.dbf files and your trend data files. Naturally your disk space usage will increase in changing periodic trends to event trends. You need to ensure enough free disk space exists.

- Citect.ini - The first task is to navigate to the CitectSCADA citect.ini or drag and drop this into the form. This INI file is used to determine the selected project as well as the default trend DATA area and any custom paths used in the citect.ini [PATH] section. 
After selection the current selected project should be shown. It is possible to select another top level project using the the “Select Other” button. From V0.96 support these being in sub directories.

- Trend Scope - The next step is to use one of the selection modes. Three modes exist.

  - All periodic trends – i.e. no name filtering used, all periodic trends  are converted

  - Use trend list file – Provide a text file with a list of the trends for conversion;  names OR paths to the trend HST files. The list files suffix must be “.TXT” E.g. mytrendlist.txt which would contain entries like :

# My event trend conversion list
# Comments allowed as long as # occurs as the first character
#
C:\Program Files\Citect\CitectSCADA 7.10\Data\cpu2.HST
C:\Program Files\Citect\CitectSCADA 7.10\Data\loop1pv.HST
LOOP_2_PV

Trend file paths must be full paths and end in a .HST
Trend names are distingished as be name only and having no .HST suffix.

  - Single Period Trend – Enter the trend name or path to the HST file. As with the trend list file, the same restrictions apply for the value entered. Note: The Browse option is for trend HST files, no browse feature currently exists for selecting a trend within the trend.dbf file(s).

  - Sub directory - Next a suitable sub directory for the new event trends needs to be configured. The default is “Convert”.  After processing you will find these subdirectories IN the directory the trend was configured to be in with the new trend  data files.      [DATA]\Convert

- Action -

  - Report – A report option is available to read your selected files and report on the proportion of samples which have changed in the period trend. This can be used if the value was much below 50% to change the trend sample time. A copy of the report will be in the default DATA area in the file “TrendConvert.log”. 
Click “Process” to run the program. 
A PERIOD trend with high unique values, e.g. above 50% may not be worth moving to EVENT format unless there are other benefits.

CSV Dump – By selecting this you will get a CSV file with the textual trend event data, e.g. 
TimeStamp-YMD+GMT, TimeStamp, Value, Quality
2015/04/29-04:57:45.000+GMT, 130747570650000000, 10.000000, 112
2015/04/29-04:57:55.000+GMT, 130747570750000000, 0.000000, 112
2015/04/29-04:58:05.000+GMT, 130747570850000000, 100.000000, 112
2015/04/29-04:58:10.000+GMT, 130747570900000000, 80.000000, 112

  - Create Event Trends – 

Record format – The default setting is to create the same data size as the periodic trend. However the user can override this and make them either 2 byte or 8 bytre event trends. Naturally an 8 byte system will use up more disk space than a 2 byte system.

File Size Settings – The default mode is “Same” which menas the same settings in the periodic trend are transferred to the event trend.tion of the event trends. “Manual” mode allows you to adjust the SAMPLE PERIOD multiplier, i.e. a x2 would change a 5s periodic sample to a 10s event setting at trend setup time. Note: In this mode the multipler is applied to all trends processed. If you need greater control of this, then a smaller trend list file should be created and several tool runs made.

If “Create Event Trends” is ticked, the “Process” button kicks the conversion process off.

What would be seen at the end of the process.

## Important Tool Use Information

### Before Using

- An equivalent INI for the “[trend]AllFiles” exists which is “[TrendConvert]AllFiles”.  1 is the default as it is in CitectSCADA.  0 will create the history files on the fly. If the existing files are fairly full then using “0” will not make much of a time difference in processing. However if the existing files are using only part of the history files count, then this will be faster.

- Space – The change in disk space can be calculated by the table below. There is some overhead per file but for calculation purposes the multiplier is close enough. If a 2 byte period data file was 100k, its Event Scaled equivalent will be 600k assuming the sample period has not changed.

| Type | Bytes Per Trend Sample | File Size Multiplier |
| --- | --- | --- |
| Periodic Scaled | 2 | 1 |
| Periodic Float | 8 | 4 |
| Event Scaled | 12 | 6 |
| Event Float | 16 | 8 |

- Sample Period Time Adjustment – If you do not change this you will never have an issue in that the event count will be less than or equal to the periodic count. If you increase the sample time then you need to be sure that the events do not “overfill” the room in the event trend.

- Processing Delays – If you wait to the NEXT time period to run this utility, then data can be lost. E.g.  5 days of trends, 5 files with 24hrs in each. If you wait 3 days then only the last 2 days will end up in the new event trends.

- If you want to capture extra debug, and tick “DebugTrace” then you need to be running “DebugView” to capture this. Goggle for DebugView++ or DebugView (the Microsoft tool). Adjust filter for “TrendConvert.exe” process.

### Running

- The minimum event data file count is 2. If one periodic file was specified, the event trend will have 2 files.

- By default, all data files are created during initialization thus this stage may take quite some time.

- A log file “TrendConvert.log” is created in the CitectSCADA DATA directory which has a copy of the session dialog. This file grows over time and relies on the user to delete the file.

- An XML file “TrendConvert_<first_trend>.xml” is created in the CitectSCADA DATA directory which has the changes to the trend records. This can be used by a macro in Excel to update records.  If CPU2 was the first trend in the processing list , then the xml file will be “TrendConvert_CPU2.xml”.
Note: Unlike the log which grows, the XML file is created on EACH run. The file will be over written when a subsequent run is done with a first trend with the same name.

### After

The typical steps needed to use these files would be:

- It is assumed backup exists of existing files and trend.dbf’s.

- Move “Convert” sub directory files into the DATA directory above (or whatever name you gave to the sub directory)

- Update the Trend.DBF records for the new EVENT trend settings (this is where “TrendConvert.xml” can be used). The macro Excel_Row_Updates() in SAVE_DBF2.XLS can be used to automate this task. See hints in the next section.

- Re-compile your project, run

### EXCEL DBF Updates

A new macro “Excel_Row_Updates” has been added to the previous CitectSCADA SAVE_DBF.XLS macros and has been saved as SAVE_DBF2.XLS. This has been tested in Excel 2003 and 2007.

Use instructions:

- Open your trend.dbf file and then open SAVE_DBF2.XLS. If prompted with a security warning, click on “Enable Macros”. Then Tools-> Macro->Macros and select Excel_Row_Updates.

- You will be prompted with a File Dialog box. Select the TrendConvert_xxx.xml file (typically in CitectSCADA xxx\Data)

- Now if you have ONE trend.dbf file in use (as include projects can each have their own trend.dbf file) then the macro should update the trend.dbf with all converted records. In this example the update was partial because another trend.dbf file exists.

- Do a visual check of the SAMPLEPER, TYPE, FILES and STORMETHOD columns for the updates to these.

- Save the trend.dbf file using the usual save macro and open the next trend.dbf file (if this applies).

Known Issues:

- You may get an error if the macro thinks the trend.DBF is not the active workbook. To fix this just click on a field in the trend.dbf and run the macro again.

- Hour glass – If you move the cursor outside a popup box, you get a BUSY ICON. This is a bit confusing as Excel is not busy, it is just the way it handles macros. By simply entering the popup or clicking OK the busy icon will go away.

## Problem Suggestions / FAQ

- Citect.ini - The program believes what is in the citect.ini. Thus if the project has been copied somewhere then a copy of citect.ini can be used for the utility. This would allow conversions to be done on another PC. We do not recommend doing this on a running CitectSCADA system as this has not been tested and also the intense CPU and disk access of the tool may cause the running CitectSCADA to be starved of resources. 
Important INIs used by the tool are : 
 - [CTEDIT] Run
 - [CTEDIT] DATA
 - [CTEDIT] User
 - [TrendConvert] AllFiles

- Utility Won’t Run – We recommend using the Dependency Walker http://www.dependencywalker.com/ to diagnose startup issues. Having installed this, drag and drop TrendConvert.exe into it. This may highlight the issue.

- Memory use – The tool reads all the various settings for the trends select prior to the processing. Thus memory use will climb based on the number of trends selected. The tool has been tested on 2000 selected trends. In memory use becomes an issue, and then you may need to do several lower trend count  conversion runs.

- Trail – We suggest a single trend is trialed first so users can get familiar with how the tool works before embarking on a full conversion. In the example on the 1st page, we ran the tool on the LOOP_2_PV  trend.  Then we  added a copy of the LOOP_2_PV trend then added “_E” to the Name, changed the Type, and adjusted the File Name. A fresh compile and then a run.

Then both trends can be viewed at the same time and should overlap. Note: Because nothing is driving the Event trend, expect that the runtime periodic trend to continue to change while the event trend remains fixed.

And briefly tested on a pre release v7.20.

Tool tested so far under v6.10 & v7.10