# Citect Trend Groups Feature

Citect Trend pages can be pre-configured to display a set of up to 8 pens. Each time the page is displayed, those pens will appear. Trend pages can also be displayed with a command like PageTrend() that displays a trend page with any specified set of trend tags. However, these can be cumbersome to use if large numbers of trends are used or the groupings change frequently.

The Trend Groups feature allows you to add a button to any trend page. When the button is left-clicked, a menu appears as shown above, listing all available groups of trend tags. Clicking on any group name displays those pens (and custom scales, if configured). Right-clicking on the menu button allows groups to be edited in the Citect runtime. A checkmark is shown next to the currently displayed group. The tool tip of the menu button will also indicate the current group.

If many trend groups are required, they may be divided into sub-menus under the main menu.

Groups are stored in a database that may be located in the project folder, the data folder, or any other location. Multiple PCs may share the same database or each may have its own unique set of groups.

## Adding Trend Groups Functionality to a Project

- Copy these files into the Citect project folder:

| TrendGroups.ci | Cicode functions |
| --- | --- |
| GroupsFormat.cii | Database format definition |
| Trends.ctm | Genie library |
| Trends.frm | Genie form definition |
| Icons.ctl | Symbol library |
| TrendGrp.dbf | Blank trend group definitions database |
| CtUtil.ci | DLL function wrappers (not needed in Citect 5.42) |

- Copy CtUtil.dll to the Citect\Bin folder. (This is not necessary in Citect 5.42 where it is already included.)

- In the Citect Project Editor, System menu, select Devices. Enter the following device definition and click Add. Specify a path/filename that will be valid from all Citect PCs.

- Paste the Trend Groups genie on a trend page

  - Open the trend page in the Citect Graphics Builder

  - In the Edit menu select ‘Paste Genie…’

  - Select the Trends library and the TrendGroups genie

  - Fill in the Genie Form that appears

    - Trend AN – Hold the Control key while double-clicking on the trend graph. The Access (General) tab will show its ‘Object AN’. Enter this value for the ‘Trend AN’ as seen below

    - Menu Button AN – Hold the Control key while double-clicking on the group menu button (). The title of the properties window will say “Button Properties”. If not, click on a blank area of the page, then Control-double-click on the menu button again.

    - Sort List – Select TRUE to have the menu sorted alphabetically. Select FALSE to leave items in the order they appear in the database

    - Edit Privilege – Set to the security privilege level (1-8) desired to be able to edit groups. Set to 0 if no security is desired.

    - Trend Select Button ANs – Entering the ANs of the 8 trend select buttons at the top of the trend page allows their tool tips to be set whenever a trend group is selected. Hold the Control key while double-clicking on each trend pen select button (). Enter the AN number as seen below.

  - Click OK to close the genie form and any other open forms

  - Move the menu button anywhere on the page as desired. It is shown in the above picture immediately to the left of the Select Pen button.

  - Save the page.

  - Run the project.

  - Right-click on the menu button to edit groups. Once groups exist, left-click to select a group.

## Managing Trend Groups

The following sections show how to create, edit, delete, copy, and rename groups.

### Creating Groups

- Right-click on the trend groups menu button. The Select Trend Group form appears.

- Click the Add button to add a new group.

- Enter a group name when prompted. Group names must be unique and cannot contain any of the following characters: ! ~ [ ] ,

- The Edit Group form will appear:

- Select any of the 8 pens as desired.

- Min and max scale may be entered to override the default.

- Menu is optional. See “Sub-menus” section below.

- Comment is optional and is only used on this form.

- Click OK to save the group.

### Editing Groups

- Right-click on the trend groups menu button. The Select Trend Group form appears.

- Select a group from the drop-down list.

- Click OK. The Edit Group form will display the settings for that group.

- Make any desired changes and click OK to save the group.

### Deleting Groups

- Right-click on the trend groups menu button. The Select Trend Group form appears.

- Select a group from the drop-down list.

- Click OK. The Edit Group form will display the settings for that group.

- Click Delete.

### Copying Groups

- Right-click on the trend groups menu button. The Select Trend Group form appears.

- Select a group from the drop-down list.

- Click OK. The Edit Group form will display the settings for that group.

- Click Copy.

- Enter the new group name when prompted.

- The Edit Group form will re-open with the new group name and all the settings of the previous group.

- Click OK to save

### Renaming Groups

- Right-click on the trend groups menu button. The Select Trend Group form appears.

- Select a group from the drop-down list.

- Click OK. The Edit Group form will display the settings for that group.

- Click Rename.

- Enter a new name when prompted.

- Click OK to save the change.

### Using Sub-Menus

By default, all groups are listed together in one menu. If this is not convenient, they may be divided into sub-menus as shown here.

- Right-click on the trend groups menu button. The Select Trend Group form appears.

- Select a group from the drop-down list.

- Click OK. The Edit Group form will display the settings for that group.

- Type a sub-menu name in the Menu field. For example, the picture above shows a group called “Pressures” that is configured with the menu name “Building 2”

Note: All groups must have unique names. For example, the Building 1 menu couldn’t have a group named “Pressures”.

## Advanced Features and Tips

Advanced users may wish to take advantage of the following features, such as selecting groups by Cicode and editing trend groups in the Citect Project Editor, as well as usage tips.

### Cicode Functions

It is not necessary to use the Trend Groups genie. Alternatives are:

- Call TrendGroupSelectMenu(hTrendAN, hButtonAN, iMode, hAN1…hAN8). This displays the same menu as the genie does. See documentation in TrendGroups.ci for details

- Call TrendGroupSelectForm(hAN, hAN1…hAN8). This displays a form instead of the drop-down menu. The form can display up to 64K of items, but shows all groups together (sub-menus are ignored).

- Call TrendGroupSelect(hAN, sGroup, hAN1…hAN8). This allows selection of a trend group without any popup form.

- Call TrendGroupMaintenanceForm(). This displays the same forms as right-clicking on the genie does.

### Citect Versions

This project is designed for Citect 5.21.

In Citect 5.42, the Citect Utility functions are built in, so it is no longer necessary to copy in the CtUtil.dll and CtUtil.ci files.

It should be possible to use trend groups in previous releases of Citect (5.0 and higher). However, it may be necessary to re-create the genie. In releases prior to 5.0, it will be necessary to create a LeaveCriticalSection() function as is found in the Citect v5 Include project.

### Limits

- Menus are limited by the Utility DLL to 50 items each. For example, the main menu could have 30 groups and 20 sub-menus (or any combination totaling 50). Each sub menu could have up to 50 items as well.

- The total number of groups must be 479 or less because of the maximum Cicode string array size.

If these limits are exceeded, the message “Too many items to show (max 50)” will appear at the bottom of the affected menu.

### Tips

- A group may be displayed automatically on page entry by calling TrendGroupSelect() from the Page Entry event. However, it may be necessary to call Sleep(x); first to allow the trend object to initialize. The optimal value for x will vary from system to system.

- After deleting a trend group, the database is automatically packed to remove the record. If Project Editor integration is enabled (see below), packing the project from the Project Editor will also pack the groups database.

- In systems with a large number of trend tags it may take a while to display the Edit Group form as all trend tags must be loaded into each of the 8 combo boxes.

- Trend tag names are read from _trend.rdb, so it doesn’t matter if they’re defined in the main project or in included projects (or both).

- If the group database (TrendGrp.dbf) does not exist, it will be created automatically when the Trend Groups feature tries to access it. However, Citect 5.21 is not able to create it automatically, so it is necessary to use the blank TrendGrp.dbf file that is included with the Trend Groups example project.

- This feature will only work with the Internet Display/Manager Client (IDC) feature if the TrendGrp.dbf file is accessible to the IDC PC. E.g. the TrendGroups device points to a local path and the file is manually copied there. Any modifications will not be seen by other nodes in this case.

- This feature is not currently redundant. If the main database (pointed to by the TrendGroups device) is not accessible, trend groups will not appear.

- If a local path is used for the TrendGroups device, changes made by one PC will not be seen by others since they’ll each have their own file. To avoid this, set the path to a network drive accessible by all nodes.

- When using Project Editor Integration, press F2 to see the extended option (the Menu field).

### Project Editor Integration

It is possible to add an Edit Group form to the Citect Project Editor to allow for editing groups offline.

Warning: This requires editing Citect\Bin\Citect.frm. Editing Citect.frm incorrectly can cause the Project Editor to fail to open. Citect Support does not support changes made to this file. Do so at your own risk. Make a backup copy of Citect.frm before editing it. Re-installing Citect, installing service packs, or upgrading Citect may overwrite Citect.frm without warning. It will be necessary to re-do any customizations afterwards.

- Open Citect\Bin\Citect.frm in Windows Notepad.

- Insert the following form definition after the trend tags definition:

FORM "Trend Groups", "Trend Groups", "trendgrp", NONINDEX;

1:      "Group",        32, readwrite_foreign;

2:      "Pen1",         32, readwrite_foreign, "Trend Tags", "NAME";

3:      "Min1",         11, readwrite_foreign;

4:      "Max1",         11, readwrite_foreign;

5:      "Pen2",         32, readwrite_foreign, "Trend Tags", "NAME";

6:      "Min2",         11, readwrite_foreign;

7:      "Max2",         11, readwrite_foreign;

8:      "Pen3",         32, readwrite_foreign, "Trend Tags", "NAME";

9:      "Min3",         11, readwrite_foreign;

10:     "Max3",         11, readwrite_foreign;

11:     "Pen4",         32, readwrite_foreign, "Trend Tags", "NAME";

12:     "Min4",         11, readwrite_foreign;

13:     "Max4",         11, readwrite_foreign;

14:     "Pen5",         32, readwrite_foreign, "Trend Tags", "NAME";

15:     "Min5",         11, readwrite_foreign;

16:     "Max5",         11, readwrite_foreign;

17:     "Pen6",         32, readwrite_foreign, "Trend Tags", "NAME";

18:     "Min6",         11, readwrite_foreign;

19:     "Max6",         11, readwrite_foreign;

20:     "Pen7",         32, readwrite_foreign, "Trend Tags", "NAME";

21:     "Min7",         11, readwrite_foreign;

22:     "Max7",         11, readwrite_foreign;

23:     "Pen8",         32, readwrite_foreign, "Trend Tags", "NAME";

24:     "Min8",         11, readwrite_foreign;

25:     "Max8",         11, readwrite_foreign;

26:	"Comment",      64, readwrite_foreign;

27:	"Menu",		 32, readwrite_foreign;

NORMAL

"Trend Group Name  {1                                                  }

Min Scale            Max Scale

Pen 1    {2                               } {3          } {4          }

Pen 2    {5                               } {6          } {7          }

Pen 3    {8                               } {9          } {10         }

Pen 4    {11                              } {12         } {13         }

Pen 5    {14                              } {15         } {16         }

Pen 6    {17                              } {18         } {19         }

Pen 7    {20                              } {21         } {22         }

Pen 8    {23                              } {24         } {25         }

Comment  {26                                                          }"

EXTENDED

"Trend Group Name  {1                                                  }

Min Scale            Max Scale

Pen 1    {2                               } {3          } {4          }

Pen 2    {5                               } {6          } {7          }

Pen 3    {8                               } {9          } {10         }

Pen 4    {11                              } {12         } {13         }

Pen 5    {14                              } {15         } {16         }

Pen 6    {17                              } {18         } {19         }

Pen 7    {20                              } {21         } {22         }

Pen 8    {23                              } {24         } {25         }

Comment  {26                                                          }

{LINE, 113}

Menu     {27                                                          }"

- After the line “"&Groups", 37, "Groups", "", "Opens the groups form";”, insert the following menu definition:

"&Trend Groups", 0, "Trend Groups", "", "Opens the trend groups form";

- Re-open the Citect Explorer. The Project Editor should now show ‘Trend Groups’ below ‘Groups’ in the System menu.

Note: This feature requires that the Trend Groups database is located in the project folder and is named trendgrp.dbf.